Table 1: Example of differential air particle count (APC) readings from various clean areas (ORs, SCT, BSC)

| Location | Date | (0.3 um) | (0.5 um) | (1 um) | (3 um) | (5 um) | (10 um) | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Stem Cell Transplant Unit SCT6 room | 22/01/2015 | 879 | 80 | 13 | 2 | 1 | 2 | Satisfactory |
| Stem Cell Transplant Unit SCT4 | 22/01/2015 | 25165 | 2981 | 111 | 6 | 2 | 1 | Check booster fan status; air filters; cleanliness |
| Operating Room (OR 3) | 19/02/2015 | 374 | 279 | 251 | 91 | 32 | 9 | To check cleanliness, air velocity |
| Operating Room OR 7 | 19/02/2015 | 123 | 8 | 3 | 3 | 1 | 4 | Satisfactory |
| Biological safety cabinet | 09/04/2015 | 0 | 0 | 0 | 0 | 0 | 0 | Satisfactory |
| Laminar Flow Hood | 09/04/2015 | 0 | 0 | 0 | 0 | 0 | 0 | Satisfactory |